[image: image8.png]111





Example Measurement & Verification Plan

for a

Super ESPC Project

8 January 2007
Federal Energy Management Program (FEMP)

Office of Energy Efficiency and Renewable Energy

U.S. Department of Energy

This document was developed for the U.S. Department of Energy’s Federal Energy Management Program by Nexant, Inc., and Lawrence Berkeley National Laboratory. This document WILL BE posted on FEMP’s web site at http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html.



Contents

71.
Executive Summary / m&v Overview & proposed savings calculations


71.1
Proposed Annual Savings Overview


81.2
M&V Plan Summary


92.
Whole Project Data / Global Assumptions


92.1
Risk & Responsibility


92.2
Energy, Water, and Operations & Maintenance (O&M) Rate Data


102.3
Schedule & Reporting for Verification Activities


102.4
Operations, Preventive Maintenance, Repair, and Replacement Reporting Requirements


102.5
Construction Period Savings


112.6
Status of Rebates


112.7
Dispute Resolution


123.
ECM 1- Lighting M&V PLAN AND SAVINGS CALCULATION METHODS


123.1
Overview of ECM, M&V Plan, and Savings Calculation


133.2
Energy and Water Baseline Development


133.2.1
Fixture Power


133.2.2
Usage Group Operating Hours


143.2.3
Sample Sizes


163.2.4
Results


173.3
Proposed Energy & Water Savings Calculations and Methodology


193.4
Operations and Maintenance and Other Cost Savings


193.5
Proposed Annual Savings for ECM


193.6
Post-Installation M&V Activities


193.7
Performance Period Verification Activities


214.
ECM 2 - EMCS M&V PLAN AND SAVINGS CALCULATION METHODS


214.1
Overview of ECM, M&V Plan, and Savings Calculation


224.2
Energy and Water Baseline Development


234.3
Proposed Energy & Water Savings Calculations and Methodology


244.4
Operations and Maintenance and Other Cost Savings


244.5
Proposed Annual Savings for ECM


244.6
Post-Installation M&V Activities


254.7
Performance Period Verification Activities


275.
ECM 3 - Chiller Replacement M&V PLAN AND SAVINGS CALCULATION METHODS


275.1
Overview of ECM, M&V Plan, and Savings Calculations


295.2
Energy and Water Baseline Development


315.3
Proposed Energy & Water Savings Calculations and Methodology


325.4
Operations and Maintenance and Other Cost Savings


325.5
Proposed Annual Savings for ECM


325.6
Post-Installation M&V Activities


325.7
Performance Period Verification Activities




Background

This document is a comprehensive M&V Plan for a fictional energy performance contract project. This document is intended to serve the following purposes:

· Provide examples of M&V Plans for common ECMs that comply with the requirements set forth in the FEMP M&V guidelines, Version 2.2
, and

· Provide and promote use of a consistent format for M&V Plans for Federal ESPC projects, as detailed by the M&V Plan Outline
.

This document contains M&V Plans for three measures, using Options A and B, at a fictitious federal office building. The ECMs include lighting, energy management and control system (EMCS) installation, and a chiller retrofit:

· Lighting Efficiency Measure – Option A, FEMP Method LE-A-02
· Energy Management Control System Installation – Option B, FEMP Method GVL-B-01

· Chiller Replacement Measure – Option B, FEMP Method CH-B-02

Measurement and Verification Plan

for the

Piscataway Federal Center

General Services Administration

Provided in fulfillment of SuperESPC requirements,

Delivery Order Number FAKE34621

By

ABC Engineering, Inc.

April 1, 2003

Project contact information:

	ABC Engineering, Inc.
	General Services Administration

	Arnold Buchstaubner
	Richard Handy

	M&V Specialist 
	Sr. Engineer

	ABC Engineering, Inc.
	Dept. General Services

	24630 Corporate Road
	Federal Center Building

	Suite 400
	1800 Highrise Road

	Boulder CO, 80302
	Piscataway NJ, 10012

	Phone (303) 988-1254
	Phone: (201) 455-3667

	Fax (303) 988-1202
	Fax: (201) 455-3439

	Email: axb@abceng.com
	Email: rihandy@piscataway.gsa.gov

	
	

	Department of Energy Representative
	General Service Administration Contracting Officer

	Tom Hattery
	Jen. A. Signatory

	Federal Energy Project Financing Specialist
	Federal Contracting Officer

	Department of Energy
	General Service Administration

	
	Federal Center Building

	
	1800 Highrise Road

	
	Piscataway NJ, 10012

	Phone: 303.829.2061
	Phone: (201) 455-3669

	Fax:301.829.7420
	Fax: (201) 455-3439

	Email: thomas.hattery@ee.doe.gov
	Email: jasignatory@piscataway.gsa.gov


1. Executive Summary / m&v Overview & proposed savings calculations 
1.1 Proposed Annual Savings Overview 

The goal of this project is to achieve energy savings through upgrades to the building’s lighting, improvements to the central plant chiller, and the addition of an energy management control system (EMCS). This project will also result in improved lighting levels and more reliable HVAC and central plant operation, thereby reducing maintenance costs. Chiller operations and maintenance savings of $12,000 is due to the replacement of a service contract with an ABC service contact as part of this Delivery Order. The $12,000 represents a net reduction in annual service expenses. Savings from the energy conservation measures (ECMs) included in the project are summarized in Table 1.1.
Table 1‑1: Proposed Annual Savings Summary

	ECM
	Electric energy savings (kWh/yr)
	Electric demand savings (kW-yr)*
	Natural gas savings (therms)
	Water savings (gallons/yr)
	Total energy savings (MBtu/yr)
	Total energy & water cost savings, Year 1 ($/yr)
	O&M cost savings, Year 1 ($/yr)
	Total cost savings, Year 1 ($/yr)

	Lighting
	186,406
	690
	0
	0
	636
	$15,339 
	$0 
	$15,339 

	EMCS
	899,252
	0
	0
	0
	3,069
	$23,841 
	$0 
	$23,841 

	Chiller
	194,119
	502
	0
	0
	663
	$14,230 
	$12,000 
	$26,230 

	Total
	1,321,032
	1,191
	0
	0
	4,368
	$53,410 
	$12,000 
	$65,410 


Utility usage for site during the period from January to December 2002 are compared to project savings in Table 1.2. 

Table 1.2 Site Use and Savings Overview

Table 1‑2: Site Use and Savings Overview
	 
	Electric energy (kWh/yr)
	Electric demand (kW-yr)*
	Natural gas  (MBtu/yr)
	Other energy (MBtu/yr)
	Water (kGal/yr)
	Total energy (MBtu/yr)

	Total proposed project savings
	1,321,032
	1,191
	0
	NA
	NA
	4,509

	Usage for entire site
	9,195,271
	31,890
	0
	NA
	NA
	31,383

	% Total site usage saved
	14.4%
	3.7%
	
	
	
	14.4%

	 
	 
	 
	 
	 
	 
	 

	Project square footage (KSF)
	                        664 
	 
	 
	 
	 
	 

	Total site square footage (KSF) 
	                        664 
	 
	
	
	
	 

	% Total site area affected
	100%
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 

	Notes
	 
	 
	 
	 
	 
	 

	MBtu = 106 Btu = 293 kWh
	
	
	
	
	 

	*Annual electric demand savings (kW/yr) is the sum of the monthly demand savings. 

	KSF  = 103 square feet.
	
	
	
	
	 

	If energy is reported in units other than MBtu, provide a conversion factor to MBtu for link to delivery order schedules  (e.g. 0.004313 MBtu / kWh).


1.2 M&V Plan Summary

ABC Engineering will perform measurement and verification (M&V) activities for each of the three ECMs in order to estimate the actual cost savings achieved in the project. The M&V plans for the three ECMs are described in Sections 3 through 5 of this document, and are summarized in Table 1.3 below. 

Table 1‑3: M&V Plan Summary

	ECM
	ECM description
	M&V option used*
	Summary of M&V plan

	Lighting
	Retrofit existing lighting fixtures w/ T-8 lamps, elec. ballasts
	LE-A-02
	Measured fixture wattages; short-term monitoring of operating hours.

	EMCS
	Install EMCS for automated control of HVAC systems 
	GVL-B-01
	Instantaneous power measurements; stipulated baseline operating hours, monitored post-installation operating hours.

	Chiller
	Replace chiller
	CH-B-02
	Baseline and post-installation kW metering.


* M&V options cited are from FEMP M&V Guidelines: Measurement & Verification for Federal Energy Projects, Version 2.2.
2. Whole Project Data / Global Assumptions

2.1 Risk & Responsibility 

The Risk and Responsibility Matrix is located in the Appendix of this document.

2.2 Energy, Water, and Operations & Maintenance (O&M) Rate Data

Energy costs used to determine the value of the energy savings are based on the rates that the facility is paying as of January 2004. The Federal Building purchases both electricity and gas from Public Service Electric & Gas (PSE&G). Electricity is provided under rate schedule GS-1. The energy rates will be escalated to account both for inflation and for changes to the real price of energy as anticipated by NIST.  In order to remain conservative without unnecessarily lengthening the term of the contract, it was decided to use the Census Region 1 fuel price indices with an assumed 3% inflation rate. Applying the NIST
 Indices to the current electric rates determines the effective rates for the duration of the contract, and is shown in Table 2‑1. NIST presumes that energy prices will fluctuate in constant dollars over the course for the contract period, and decrease in some years relative to 2003, the base year. When an inflation rate is added to the energy price indices, the effective escalation rate is 2.9% annually over the contract term.
If energy prices increase at a greater rate, then the agency will realize more savings than will be claimed. The agency also needs to realize that in the unlikely event that energy prices do not increase as predicted, the energy saved will still be valued at these rates. 

Table 2‑1: Electric Rate Escalation Schedule of GS-1 Rate
	Contract Year
	Year
	Index
	kWh
	kW

	0
	2003
	1.00
	$0.0525
	$8.052

	1
	2004
	1.02
	$0.0536
	$8.215

	2
	2005
	1.03
	$0.0541
	$8.296

	3
	2006
	1.03
	$0.0541
	$8.296

	4
	2007
	1.04
	$0.0546
	$8.377

	5
	2008
	1.06
	$0.0557
	$8.540

	6
	2009
	1.09
	$0.0573
	$8.784

	7
	2010
	1.13
	$0.0594
	$9.109

	8
	2011
	1.18
	$0.0620
	$9.516

	9
	2012
	1.23
	$0.0647
	$9.923

	10
	2013
	1.27
	$0.0668
	$10.248

	11
	2014
	1.31
	$0.0689
	$10.573

	12
	2015
	1.36
	$0.0716
	$10.980

	13
	2016
	1.42
	$0.0748
	$11.468

	14
	2017
	1.47
	$0.0774
	$11.875

	15
	2018
	1.54
	$0.0806
	$12.363


2.3 Schedule & Reporting for Verification Activities 

The schedule of M&V submissions is summarized in Table 2.2. 

Table 2‑2: Schedule of Verification Reporting Activities
	Item
	Time of submission
	Owner’s review and acceptance period

	Post-Installation Report
	30 days after acceptance
	30 days

	Annual Report
	30 days after annual performance period
	30 days


The Post-Installation Report will be submitted within 30 days of project completion. The Federal Building’s representative will then have 30 days to review and approve the Post-Installation Report. Commissioning will be reported separately. After receipt of the Post-Installation Report, GSA will issue ABC Engineering a written notification of acceptance. 

The Post-Installation Report will document any deviations from the specified equipment and, if necessary, make adjustments to the energy savings calculated herein. The Post-Installation Report will follow the format and content defined for Super ESPC projects. The specific items that will be reported are described in the M&V plan for each ECM.

The Annual Report will be due within 30 days of the end of the annual performance period. The Federal Building’s representative will have 30 days to review and approve the Annual Report. The Annual Report will follow the format and content defined for Super ESPC projects. The specific items that will be reported are described in the M&V plan for each ECM.

2.4 Operations, Preventive Maintenance, Repair, and Replacement Reporting Requirements

ABC Engineering will report on all maintenance work completed in the Annual Report. GSA will continue to maintain maintenance records per existing procedures, and will make these records available to ABC Engineering upon request.
2.5 Construction Period Savings

No construction period savings have been claimed.

2.6 Status of Rebates 

Prescriptive rebates are available from New Jersey’s Clean Energy Program
 for lighting efficiency upgrades.  The table below lists lighting incentives available for this project. ABC Engineering has submitted an application on behalf of the GSA to PSE&G to receive rebates for the lighting efficiency measure. Incentives will be provided directly from PSE&G to the GSA.
Table 2‑3: Lighting Rebates from Public Service Electric & Gas
	Fixture type
	# Fixtures
	Rebate $ / fixture
	Total rebate

	T-8, 4-lamp
	1,347
	$10 
	$13,470 

	T-8, 2-lamp
	94
	$10 
	$940 

	Screw-in CFLs
	307
	$0
	$0 

	Exit Sign LEDs
	39
	$20 
	$780 

	TOTAL
	1,745
	 
	$15,190 


2.7 Dispute Resolution

The procedures defined in this measurement and verification plan should prevent any disputes. In the unlikely event that a dispute does arise regarding issues such as baseline adjustments or use of measured data, the issues will be jointly reviewed and an agreeable resolution reached. Otherwise, the arbitration clause in the Management Plan of the Delivery Order will apply.
3. ECM 1- Lighting M&V PLAN AND SAVINGS CALCULATION METHODS

3.1 Overview of ECM, M&V Plan, and Savings Calculation  

A complete retrofit of the lighting equipment in the Federal Center is planned as a part of the ESPC agreement. The existing T-12 fluorescent fixtures (1,745 total) will be retrofitted with more efficient equipment, primarily T-8 lamps and electronic ballasts. Energy savings and demand savings will result from this retrofit. An additional benefit will be enhanced quality of lighting, as the new fixtures will provide improved color rendering and reduced flicker. 

Option A has been selected for this retrofit due to the measure’s relatively small cost savings contribution of all the retrofits installed at the Federal Center and due to the high confidence with which the fixture demand and operating hours may be determined. Equipment numbers and locations will not vary and operating hours are not projected to change after the project is implemented.

The Measurement and Verification Plan for the lighting efficiency retrofit at the Federal Center will follow FEMP M&V Option A, Method LE-A-02. The variables affecting savings from this lighting project are fixture powers, hours of operation, and level of coincident operation (% operation when the building peak demand is set). Fixture powers will be measured on a sample of the most common fixture types. For less common fixture types, fixture power will be based on a table of standard fixture powers or manufacturer’s data. 

Operating hours will be measured on a sample of space types during the Detailed Energy Survey. The measured hours will then be used to estimate the energy and demand savings during performance period and will not be adjusted even if the actual operating schedules change.  

The Measurement and Verification Plan for this retrofit assumes: 

· Operating hours will be measured before the retrofit. The hours for the lighting fixtures will be the same before and after the equipment retrofit for the purpose of energy savings calculations.

· Fixture powers before and after the retrofit will be measured.
· Interactive effects on heating and cooling equipment from the lighting retrofit will not be considered.

· Lighting levels will not decrease as a result of the lighting equipment retrofit. Existing lighting levels have been measured and recorded for each area. Results are included in the equipment inventory.

3.2 Energy and Water Baseline Development

During the Detailed Energy Survey, which took place during April 2003, a comprehensive lighting audit was completed. A room-by-room inventory of fixture counts, types, and circuits was made. This inventory of all existing lighting equipment, including lighting levels is provided in the Appendices. 

3.2.1 Fixture Power

During the lighting survey, fixture types (lamp/ballast combinations) present in this facility were identified. Samples of the most common fixture types were measured to determine the fixture power under actual operating conditions. The measured fixture types represent more than 75% of the baseline connected load. For the remaining fixture types that were not measured, fixture powers were taken from a table of standard fixture powers. The table of fixture powers to be used is from Public Service Gas & Electric as part of their rebate program.
When the fixtures are replaced, power measurements will again be taken on a sample of fixtures that represent more than 75% of the new connected load. For the remaining fixture types that are not measured, fixture powers will be taken for a table of standard fixture powers or from manufacturer specifications. 

In all cases, the number of power measurements taken is sufficient to achieve a 10% precision at 90% confidence as discussed in Section 3.2.3 Sample Size.  Because fixtures powers tend to be in close agreement with each other, usually only three measurements were required to meet this precision and confidence criteria. In some cases, three lighting circuits (rather than three fixtures) were measured where all fixtures were the same and no other loads were present. The total power measured was then divided by the number of fixtures on each circuit to determine the average fixture power. The results of the measurements are presented in Table 3‑3 in section 3.2.4.
A Fluke 39 single phase power meter was used for all measurements. Measured lighting fixtures had been operating at least one hour prior to measurement in order to achieve typical operating temperature. The Fluke was used to measure true power, which considers volts, amperes, and power factor. The Fluke is calibrated once every two years at a Fluke-authorized service center. 
3.2.2 Usage Group Operating Hours

Lighting usage groups were identified based on space functionality and estimated annual operation hours. For usage groups that represented more than 5% of the energy savings, fixture operating hours were monitored to determine the typical operating hours. Groups that represent 5% or less than the expected energy savings were not metered; operating hours were based on typical hours of occupancy. However, sufficient usage groups were monitored to account for at least 75% of the total energy savings. 

During the audit, the operating hours for a sample of lighting fixtures in each usage group was measured over a three-week period. The monitored operating hours were used to estimate the annual operating hours for each of the seven usage groups with a precision of 20% at 80% confidence. Sample size for each usage group was eleven loggers.  The measured operating hours will be stipulated as annual operating hours during the performance period. 

Hobo lighting loggers were installed inside the lighting fixtures. These loggers record the time of the change-of-state between on and off. In addition to the total operating hours recorded, logger data was evaluated to determine the number of hours that a fixture was operating between 1:00 and 4:00 PM. This information was used to estimate the probability that fixtures in each usage group would be operating coincident with the building peak load. This data was used to determine an overall peak coincidence factor for the lighting. The results of the measurements are presented in Table 3‑3  in Section 3.2.4.
The Hobo loggers have a light threshold range of 10 to 300 lumens/ft2 under fluorescent light (the sensitivity to incandescent light is about ten times greater.) The lighting loggers record on-off times with an accuracy of ±1 minute per week. The internal clock is synchronized to the computer’s clock when the logger is launched Calibration is not necessary. The results of the metered data are summarized in the following section and all metered data are included in the Appendix.

3.2.3 Sample Sizes
Appendix D.3.2, Usage Group Sampling, in the FEMP M&V Guidelines (V 2.2, 2000) describes the details of the method used to determine the sample size for each usage group or fixture type measurement. These procedures apply to groups used to determine operating hours and fixture powers. Precision and confidence criteria were selected based on experience with previous projects and represent a reasonable compromise between desired precision and cost-effectiveness.  
A sample of monitoring points for each usage groups was determined by the following procedure:

1. Define the desired precision and confidence for each measured parameter. For measuring fixture powers, +10% precision at 90% confidence is desired. A high degree of precision is required because new fixture powers are subtracted from the existing fixture powers. Both need to be known with a high degree of precision in order to reduce the uncertainty in the difference. For measuring usage group operating hours, +20% precision at 80% confidence was selected because: 1) the ESCO is not responsible for usage characteristics, and; 2) it is not cost-effective to reduce uncertainty further. 

2. Since sample size required to meet stated precision and confidence criteria is dependent on the actual measurement results, assume an initial coefficient of variation for each measured parameter. For existing fixture power, use Cv = 0.2; for new fixtures, use Cv = 0.1; for operating hours, use Cv = 0.5. 

3. Using the stated assumptions and Equation D.3 from the FEMP M&V Guidelines
, estimate the sample size n for the power and operating hour measurements. Given the assumed large size of fixtures and usage group spaces, ignore the finite population correction and  use the following standard statistical equation for estimating sample sizes:



[image: image1.wmf]2

2

v

2

p

C

Z

n

=


Equation 1
where: 


Z 
= 
Z statistic for desired confidence interval 

p 
=
desired precision

Cv 
=
coefficient of variation 

n
= 
sample size after rounding up to the next integer 

The coefficient of variation (Cv) is simply the standard deviation of the measurement divided by the average measurement value. 



[image: image2.wmf]x

C

v

s

=


Equation 2
where: 


 
=
standard deviation of the measurement



[image: image3.wmf]2

()

1

xx

n

s

-

=

-

å


Equation 3
x
=
individual measured values



[image: image4.wmf]x

 
=
average measured value of n samples

4. Using the stated precision and confidence levels from Step 1, determine the sample size for each fixture type and operating hour usage group using the following tables:
Table 3‑1: Initial Sample Sizes For each Usage Group

	Measured Value
	Precision
	Confidence
	Z
	Assumed Cv
	Sample Size, n

	Power, W (baseline)
	+10%
	90%
	1.645
	0.2
	11

	Power, W (new)
	+10%
	90%
	1.645
	0.1
	3

	Hours
	+20%
	80%
	1.282
	0.50
	11


The selection of assumed Cv for each measurement type is based on experience with previous projects. Power measurement sample size may be increased if field results indicate significant variability in the measurements. 

If a population of fixture types or usage groups is less than 100, refer to the FEMP Guidelines 2.2, Appendix D, equations D.3 and D.4 and Table D.2 for a discussion of how to adjust samples sizes for small populations. 
5. When taking power measurements in the field, it is not expected that the metering technician will calculate the actual Cv of the power measurements. Instead, the metering technician will compare the lowest measured value to the highest for each fixture type. If the highest measured value is more than twice the lowest measured value, the number of field measurements will be doubled for that fixture type group
.
6. Using the actual Cv , calculated using Equation 3,  the resultant precision can be calculated from the previous equations after some simple algebraic manipulation. The measurement precision can be calculated as follows:  



[image: image5.wmf]n

ZC

p

v

=


Equation 4
7. Fixture powers will be based on the average of the measured values. Usage group operating hours will be based on the average of the measured values. The coincidence factor (CF, portion of that lighting operation that coincides with building peak) for each usage group will be based on the operating hours between the building’s peak demand period of 1:00 and 4:00 PM as follows: 


[image: image6.wmf]Period

Peak

building

in

hours

of

Number

Period

Peak

Building

during

Hours

Operating

Measured

CF

UsageGroup

=


Equation 5
8. Using the demand savings and measured operating hours, estimate the annual energy savings from each usage group.

3.2.4 Results
Fixture power measurements are listed in Table 3‑2 below. The number of fixtures in each group, the contribution to the total connected load (for baseline fixtures only), power from standard table, power measurements, sample size, and precision are all provided. 

Table 3‑2: Fixture Wattage Measurements – Types, Monitoring Points, Results

	Fixture Type
	Number of fixtures
	% of Energy Savings
	Table Power, W
	Number of Measurements 
	Average Measured Power, W
	Std Dev, W
	Actual Cv
	Precision at 90% confidence

	F44EE
	1,000
	70%
	144
	11
	140
	11.2
	0.08
	4.0%

	F42EE
	60
	9%
	72
	11
	74
	3.7
	0.05
	2.5%

	F82ES
	339
	7%
	128
	11
	120
	18.0
	0.15
	7.4%

	75 Watt Inc.
	307
	10%
	75
	11
	75
	4.5
	0.06
	3.0%

	Inc. Exit Signs
	39
	2%
	22
	
	
	
	
	

	Totals
	
	98%
	
	
	
	
	
	


The fixture groups and metering results are shown in Table 3‑2 above. The number of samples in the Exit signs was set to zero because of their small contribution to the overall savings. Since the actual Cv was less than the assumed value of 0.2 in all cases, the precision criteria has been met.  
The operating hours for three usage groups were monitored for a three-week period in April – May 2003. The average annual operating hours for each usage group are shown in Table 3‑3, along with the actual Cv of each group. The table shows that the estimated Cv for two of the groups was less than the assumed value of 0.5 and so the precision criteria for those two groups was met. For the closed office areas, the large variability in usage resulted in a Cv greater than 0.5 and an initial precision of 24% with eleven samples. Additional monitoring was not conducted. 
Table 3‑3: Usage Group Descriptions, Monitoring Points & Results
	Usage Group
	Number of fixtures
	# Circuits (N)
	# Points (n)
	Demand savings, (kW)
	Annual op. hours
	Energy savings, kWh
	% of total
	Cv
	Precision at 80% confidence
	Coincidence 1 – 4 pm

	24 Hour - Exit
	69
	21
	0
	0.82
	Est. 8,760
	7,169
	4%
	 
	 
	 

	24 Hour - Misc
	30
	19
	11
	1.78
	8,760
	15,598
	8%
	0.2
	7.6%
	72%

	Closed Office Areas
	673
	204
	11
	22.96
	1,900
	43,377
	23%
	0.65
	16.8%
	68%

	Common Office Areas
	581
	176
	11
	37.39
	2,800
	104,343
	56%
	0.43
	16.1%
	86%

	Conference Rooms
	43
	13
	0
	2.75
	Est. 1,600
	4,436
	2%
	 
	 
	 

	Halls and Common areas
	131
	37
	0
	1.56
	Est. 3,000
	4,633
	2%
	 
	 
	 

	Storage, comp. closets
	218
	66
	0
	5.57
	Est. 1,200
	6,850
	4%
	 
	 
	 

	Totals
	1745
	526
	38
	72.83
	 
	186,406
	100%
	 
	 
	79%


The weighted peak coincidence factor is used to calculate the demand cost savings from the demand savings. The demand reduction listed in Table 3‑3 is based on a reduction in the connected load. However, not all of this reduction will appear in the form of reduced demand charges on the utility bill. The coincidence factor for each usage group represents the fraction of fixtures operating when the building peak demand is set and therefore represents that usage group’s contribution to the demand reduction seen at the utility meter. 

3.3 Proposed Energy & Water Savings Calculations and Methodology

The proposed lighting energy and demand savings are calculated for each line item in the lighting audit inventory using Equations 6 and 7 below:

ES = [(FPBase x NBase) - (FPPost x NPost )] x H 


Equation 6
DS = [(FPBase x NBase) - (FPPost x NPost )] x CF x 12

Equation 7
Where:


ES
=
Annual electric energy savings (in kWh) 

DS
=
Annual electric demand savings (in kWh) 

FPBase
=
Baseline fixture power consumption (in kW/fixture) 
FPPost 
=
Post-installation fixture power consumptions (in kW/fixture) 
NBase 
=
Number of baseline fixtures

NPost 
=
Number of post-installation fixtures.
H
=
Annual operating hours

CFj
= Coincidence factor

Total energy and demand savings are the sum of the energy and demand savings for each line item. The total annual cost savings will be determined using Equation 8:

ECSTotal = ESTotal x ER + DSTotal x DR


Equation 8
Where:


ECSTotal 
=
Total annual energy cost savings (in dollars)

ER
=
Electric energy  rate (in $/kWh)

DR
=
Electric demand rate (in $/kW)

where the electric energy and demand rates are outlined in Section 2.2 Whole Project Data / Global Assumptions. 
As described in the Responsibility Matrix, no alterations or renovations to the office spaces are planned. Should the GSA make any changes, it assumes the risk that the savings calculated by this plan may not materialize. 

3.4 Operations and Maintenance and Other Cost Savings

O&M savings are not being claimed or documented for this ECM.

3.5 Proposed Annual Savings for ECM 

See detailed lighting inventory and retrofit specifications, along with savings calculations in the Appendices.

Table 3‑4: Proposed Annual Savings for ECM 1- Lighting
	 
	Electric energy use (kWh/yr)
	Electric demand (kW-yr)
	Total energy use (MBtu/yr)
	Electric energy cost, Year 1 ($/yr)
	Electric demand cost, Year 1 ($/yr)
	O&M costs, Year 1 ($/yr)
	Total costs, Year 1 ($/yr)

	Baseline use
	557,365
	2,090
	1,902
	$29,262 
	$16,832 
	NA
	$46,094 

	Post-installation use
	370,959
	1,400
	1,266
	$19,475 
	$11,276 
	NA
	$30,752 

	Savings
	186,406
	690
	636
	$9,786 
	$5,556 
	$0 
	$15,342 


3.6 Post-Installation M&V Activities

Upon completion, an as-built inventory of post-installation lighting fixtures will be supplied, including the lighting ballasts and lamps actually installed, and lighting illumination levels (foot–candles) in the areas specified. Lighting level measurements will be made in the same fashion as baseline measurements, and will be taken after at least 100 hour of fixture use.  Savings predictions will be corrected based on as-built data and will be reported in the Post-Installation Report.

Immediately following installation, fixture power will be measured in a manner identical to that for the baseline fixtures. Sample sizes for measurements and procedures are described in Sections 3.2.1 and 3.2.3. The range of highest to lowest power measurements will be calculated in the field. If the ratio exceeds 2.0, three additional measurements taken and the fixtures will be inspected to verify that the correct fixtures have been installed. These measurements will be used to calculate actual expected energy savings, and will be detailed in the Post-Installation Report.
3.7 Performance Period Verification Activities

Once per year, for each year of the contract, ABC Engineering will conduct a site visit, during which the lighting system will be inspected to verify proper operation, ensure that it has been maintained, and continues to have the potential to generate the expected savings. 

A minimum of 1% of affected floor space will be visually inspected to ensure presence of specified lighting equipment. Lighting replacement stock will be inspected during the annual site visit to ensure that the proper replacement equipment is available. 

The Annual Report will detail the results of annual inspections, noting significant problems such as burned-out lamps and ballasts and deviations with the expected number of operating fixtures, etc. The following will be data will be included in the annual report:

· Dates and times of site visits;

· ABC Engineering and GSA staff involved;

· Areas inspected and findings from inspections;

· Evaluation of lighting replacement inventory and purchase orders to determine if consistent with ABC installed equipment; 

· Number of lamp and ballast replacements made over the performance year;

· Any problems identified with the lighting systems by ABC or the GSA;

· Any major changes in facility that affect this ECM;

· Any changes in usage of lighting systems

The GSA is required to track and report to the ABC Engineering the following items each year:

· Number of lamp and ballast replacements made over the performance year;

· Any problems identified with the lighting systems by the GSA;

· Any major changes in facility that affect this ECM;

· Any changes in usage of lighting systems

4. ECM 2 - EMCS M&V PLAN AND SAVINGS CALCULATION METHODS

4.1 Overview of ECM, M&V Plan, and Savings Calculation  

A new energy management and control system (EMCS) will be installed in the Federal Center to provide enhanced control of the facility’s HVAC systems. This system will provide energy and cost savings by providing time of day control for the chiller, water circulation pumps, and air-handler fans.

Currently, the HVAC fans and pumps operate at constant speed under manual on/off control. The fan motors operate continuously and the chiller and pump motors run longer than necessary. The control system will use an “optimum start” sequence to determine the start-up time for the HVAC system, which will likely range between 4:00 AM and 6:00 AM. This sequence will evaluate indoor and outdoor conditions by taking temperature (indoor and outdoor) and humidity (outdoor) measurements and start the equipment accordingly, so that proper set-points are reached prior to occupancy. Shut-off time will be set to 9:00 PM in order to give cleaning crews time to work. 

Current heating and cooling setpoints are determined by pneumatic thermostats which are no longer calibrated and can be changed by the occupants. The current heating and cooling setpoints are not easily quantifiable, but range from 68 ºF to 76 ºF winter and summer. The new winter set-point (October – April) will be 68 (F and the summer set-point (May – September) will be 72 (F as agreed to between ABC and GSA.

The new control system will start and stop the equipment as needed, thereby reducing operating hours, and provide savings in the form of reduced kilowatt-hour consumption. Demand savings will not be realized for this measure, because the reduced operation hours will take place at night and not during daytime peak periods. 

Chiller savings due to reduced chiller runtimes will not be claimed. While the existing chiller is enabled during the evenings in the cooling season, the actual hours of evening operation are uncertain. Rather than stipulate an uncertain number of operating hours as the baseline case, savings due to reduced runtimes will not be claimed. GSA will still benefit from this reduced runtime. Operating conditions for the chiller will be monitored, but this information will be used for chiller savings verification.  
Natural gas savings from reduced heating are not included due to the difficulty in quantifying these savings.
The measurement and verification plan for the EMCS installation will follow FEMP Option B, Method GVL-B-01: generic variable load project with continuous metering. The EMCS system will be used to record the actual run time of the equipment during the performance period. 

Option B was chosen for this measure because of the concern that post-installation motor operation hours may not turn out as estimated. In addition, Option B was selected because the installation of the new control system readily lends itself to ongoing measurement. The control system can track the actual run times of equipment with great accuracy and very little added cost.

The following assumptions are employed for this M&V plan:

· In the absence of this project, the pump and fan performance would remain constant (and not degrade) at the levels measured during the detailed energy survey. This is a conservative estimate in that should motor demand levels increase, the overall effect on baseline energy consumption would be to increase, thus increasing the savings estimated for this project. 
·  Chiller savings due to reduced evening runtimes will not be claimed. 
· In the absence of this project, the operation schedule of the chiller, pump, and fan motors would remain the same, and baseline operation hours would remain constant. This assumption was based on the feedback received from the facility staff who indicated that the operation schedule had not changed for the previous five years.

· The occupied hours of the facility are assumed to remain unchanged for the duration of the project, and are Monday – Friday from 7:00 AM to 7:00 PM every day.  

4.2 Energy and Water Baseline Development

The current annual operating hours that were reported by the facility staff are shown in Table 4.1. Cooling equipment (chiller and water pumps) are enabled continuously from May through September and operate as-needed. The hot water pump operates continuously from October through April. The air handler fans operate continuously year-round. 

Table 4‑1: Equipment Baseline Operating Hours

	Equipment
	Operating period
	Annual hours

	Chiller
	Enabled May – September 24/7
	3,672

	AHU-1 supply fan
	Always on
	8,760

	EX-1 exhaust fan
	Always on
	8,760

	HWP-1 hot water supply pump
	On October – April
	5,088


Motor kW demand is assumed to remain constant for the duration of the contract. The nameplate data of each motor was recorded, and the power draw from each was measured on May 1, 2003 by ABC staff in the presence of Mr. Handy, the Federal Center Facility Manager. These values are shown in Table 4.2 below.

Table 4‑2: Equipment Nameplate Data and Measured Power Draw

	Equipment
	Nameplate data (HP)
	Nominal RPM
	Nominal voltage
	Measured power draw (kW)

	AHU-1 supply fan
	75
	1800
	480
	68.3

	EX-1 exhaust fan
	50
	1800
	480
	48.7

	HWP-1 hot water supply pump
	25
	1800
	480
	26.7


4.3 Proposed Energy & Water Savings Calculations and Methodology

The run-time data recorded by the EMCS equipment will be analyzed and summarized upon receipt on a bi-monthly basis. For each motor, during its operation period (Table 4.1), the total number of operating hours will be determined by summing the status data collected for each motor and multiplying by the data interval (15 minutes). 

Annually, Equation 4-1 and Equation 4-2 will be used to calculate the energy savings resulting from the EMCS installation for each piece of equipment listed in Table 4.1.

Equation 4-1:

Annual kWhsaved motori
= 
kWbaseline motori ( 



( Op. Hoursbaseline motori – Op. Hoursmeasured motori )

Equation 4-2:

Total Annual kWhsaved 
=  
Annual kWhsaved AHU-1 + 





Annual kWhsaved EX-1 + 





Annual kWhsaved HWP-1

The maximum operating hours expected for the equipment with the EMCS installed are listed in Table 4.4 below.  These values will be used if actual facility occupancy hours increase. 
Table 4‑3: Annual Post-Installation Operating Hours, Expected & Maximums

	Equipment
	Maximum Annual post-installation operating hours
	Expected Annual post-installation operating hours

	AHU-1 supply fan
	5,616
	4,380

	EX-1 exhaust fan
	2,070
	4,380

	HWP-1 hot water supply pump
	5,616
	2,544


Cost savings will be determined using energy rates detailed in Table 2‑1 of Section 2.2.

4.4 Operations and Maintenance and Other Cost Savings

O&M savings are not being claimed or documented for this ECM.

4.5 Proposed Annual Savings for ECM

Table 4‑4: Proposed Annual Savings for ECM 2 – EMCS

	 
	Electric energy use (kWh/yr)
	Electric demand* (kW-yr)
	Total energy use (MBtu/yr)
	Electric energy cost, Year 1 ($/yr)
	Electric demand cost, Year 1 ($/yr)
	Other energy-related O&M costs, Year 1 ($/yr)
	Total costs, Year 1 ($/yr)

	Baseline use
	1,266,002
	158
	4,321
	$66,465 
	$15,291 
	$0
	$66,465 

	Post-installation use
	811,894
	158
	2,771
	$42,624 
	$15,291 
	$0
	$42,624 

	Savings
	454,108
	0
	1,550
	$23,841 
	$0 
	$0 
	$23,841 


4.6 Post-Installation M&V Activities

The points in the new EMCS system to be monitored for use in savings calculations are listed in Table 4‑5. All of these points will be “trended” – meaning that there will be a time stamp associated with each recorded point value. From this information, the total operating hours of the affected equipment for the year will be calculated. Temperature data will be collected and analyzed to ensure that the operation of the control system is as intended. Additional points will be collected for ECM 3 (Chiller) in order that this information can be used to verify the performance of that measure. A complete listing of the EMCS system parameters will be provided in the Post-Installation Report, including:

· documentation of the actual EMCS installed, detailed sequences of operations, as-built points list, and a summarization of the EMCS operation features in regard to control of the chiller pump and fan motors, 

· operation manuals for the EMCS and chillers. 

Commissioning documentation on this ECM will be provided separately.
Table 4‑5: EMCS Control Points for Savings Calculations

	Equipment
	Type of Point

	Chiller compressor motor
	kW

	AHU-1 supply fan
	Status

	EX-1 exhaust fan
	Status

	CHWP-1 chilled water supply pump
	Status

	CWP-1 condenser water pump
	Status

	HWP-1 hot water supply pump
	Status

	Indoor air temperature
	Analog temperature sensor

	Outside air temperature
	Analog temperature sensor

	Outside humidity sensor
	Analog humidity sensor

	Chilled water supply temperature
	Analog temperature sensor

	Chilled water return temperature
	Analog temperature sensor

	Chilled water flowrate
	Analog flow meter

	Condenser water return temperature 
	Analog temperature sensor


The EMCS system will be set up to automatically write the run-time data to the dedicated control computer’s hard-drive each day at midnight. Every other month, ABC Engineering staff will remotely download that data for analysis and back-up purposes. The data will be reviewed at that time to ensure the control system is operating properly.

4.7 Performance Period Verification Activities

During the first quarter of each year (January to March) a site visit to the Federal Center will be conducted by ABC Engineering personnel. Activities to be conducted during this site visit includes verification of proper equipment and control sequence operation and measurement of power draw of the equipment listed in Table 4.1 to ensure that the equipment demand has not changed. 

The equipment that was used for taking the baseline power measurements will be used during the annual site visit to verify equipment performance has not changed. The meter to be used is a digital multi-meter, ACME model 40, which is calibrated by the manufacturer on a semi-annual basis. The meter has an accuracy of +0.5%. The meter specifications are included in the Appendices. Elite Industries thermistor sensors shall be used for taking temperature measurements.  These sensors are rated at  ±1 ºF accuracy. Cut sheets are included in an Attachment to this document. ABC will perform required equipment calibration each performance year. 
Elite Industries humidity sensors shall be used for taking humidity measurements. These sensors are rated at  ±5 % accuracy. Cut sheets are included in an Attachment to this document. Calibration will be provided each performance year. 
Ongoing quality assurance procedures for the metered run times of equipment include a bi-monthly review of the data to see if it is reasonable and corresponds to anticipated values. Raw data files will be stored separately and made available to the Agency upon request. In the case that some data are missing, a check for a valid reason for missing data will be made. If the data is truly missing, then operating hours for the period with missing data will be derived from data from a similar period. Sources of data used to make up for missing data will be clearly identified and will be described in the Annual Report.

The Annual Report will summarize the results of calculations that determine the savings. Monitored data and details of all calculations will be provided electronically in MS Excel( spreadsheets. An example spreadsheet format is provided in Table 4‑6. 
Table 4‑6: Example Monthly Calculation Format – AHU1

	Day
	Measured Operating Hours – AHU1
	kWhpost
	kWhbaseline
	kWh Savings

	1
	
	
	
	

	2
	
	
	
	

	3
	
	
	
	

	…
	
	
	
	

	…
	
	
	
	

	Totals
	Op.Hrstotal
	kWhpost total
	kWhbaseline total
	kWhsaved total


5. ECM 3 - Chiller Replacement M&V PLAN AND SAVINGS CALCULATION METHODS

5.1 Overview of ECM, M&V Plan, and Savings Calculations

As detailed elsewhere in this proposal, the Piscataway Federal Center is cooled by a central chilled water plant with a 400-ton constant-speed centrifugal chiller that is 20 years old and has experienced significant degradation in performance. The existing chiller has a nominal rated full-load efficiency of 0.85 kW/ton at ARI conditions, which is significantly poorer in comparison with efficiencies of currently available centrifugal chillers. 

As part of this ESPC project, the existing chiller will be replaced with a new, high efficiency unit with the same capacity. The proposed chiller will have a nominal full-load rating of 0.52 kW/ton at ARI conditions. Part-load performance is significantly improved due to the VFD option, which allows better part load performance than the existing chiller with inlet guide vanes. The cooling tower was replaced five years ago, and will not be modified, however, condenser water temperature will be allowed to drop below 85 ºF when the wet-bulb conditions allow. This will further improve the part-load chiller performance. The chilled water and condenser water pumps will be serviced, but not replaced. No other changes to the cooling plant will be made. Energy savings for this measure will result from the reduction of chiller demand to provide the same cooling as in the baseline case. 

FEMP Option B, Method CH-B-02 will be used to measure and verify the energy savings from this retrofit. This method requires metering of chiller electric and load variables in both the baseline and post-installation period. Baseline metering was performed over a short-term period, and continuous metering via the EMCS will be done in the post-installation period. It is appropriate to use Option B for this project for several reasons. There is a significant uncertainty in what the actual operating hours & loads of the new chiller will be, data collection is available with the use of the new EMCS (ECM 2), and analysis of the collected data will provide a continuous performance check on the new chiller.

The purpose of collecting baseline chiller data was to develop a model of the existing chiller’s performance. This model will enable the prediction of the baseline chiller demand from load and system operating parameter data. Approximately one month (August 13 to September 17, 2003) of baseline metering was conducted, with enough data points collected to successfully build the performance model. 

In the post-installation period, chiller demand (kW), load data (tons, as calculated from water temperature and flow measurements), and system operating parameters (chilled and condenser water temperatures) will be collected continuously in 15-minute intervals. The load data will be used to determine the equivalent baseline chiller demand for the same interval. Savings will be determined from the difference in the calculated baseline chiller demand and the actual post-installation chiller demand. 
The following figure will help illustrate the savings verification process:

Figure 5‑1: Overview of Chiller Savings Calculations
 [image: image7.emf]Chiller Performance and Savings

0

100

200

300

400

0 100 200 300 400

Tons

kW

kW New

kW Baseline

kW measured

ASHRAE model for 

baseline chiller

1. Measure chiller load and 

operating conditions.

2. Estimate baseline chiller demand 

at current conditions & 85F CWT

3. Measure the new chiller demand.

4. Calculate kW reduction as 

difference between baseline 

and measured values.

 Manufacturer's model for new 

chiller


9. Measure the chiller load (tons) from the chilled water supply and return temperatures and flow rates. 
10. Estimate the baseline kW demand from the model of the old chiller at current operating conditions (actual chilled water temperature, tons). The baseline condenser water temperature will be held 85 ºF since that was the steady state case in the baseline due to the old chiller’s operating limitations). 
11. Measure the new chiller demand under actual operating conditions. 

12. Calculate the demand savings for each 15-minute interval as the difference between the baseline model and the measured value. 

13. If the chiller is off, demand reduction is treated as 0 kW. 

14. Annual energy savings will be calculated as the sum of the 15-minute savings. This savings calculation assumes a minimum number of ton-hours of cooling per year. In the event that the measured ton-hours are less than a specified minimum, savings based on measured chiller performance may be adjusted upwards to reflect what would have occurred had the minimum number of ton-hours been provided. 
This M&V plan is based on the following assumptions:

· No other physical changes are planned to the condenser pumps, chilled water pumps or the cooling tower. 
· Condenser water in the baseline model will be held constant at 85 ºF. The actual condenser water temperature will be allowed to fall below 85 ºF to improve part-load performance.  
· Baseline chiller performance will be adjusted based on actual chilled water supply temperature. 
· One month of monitoring of chiller demand and load variables was adequate to develop an accurate model of the existing chiller performance. 

· The building plans no major projects, such as building additions, or changes which would significantly alter the current building occupancy rate, schedule, or other internal cooling loads.

5.2 Energy and Water Baseline Development

Data collection of the existing chiller’s demand, entering and leaving chilled water temperatures, and entering condenser water temperature occurred during August and September 2003. The data was collected in 15-minute intervals using an Elite 6-channel data recorder
. In order to collect data over a full range of operating conditions (chilled and condenser water temperatures, chiller demand) expected in the post-installation period, the condenser and chilled water temperatures were reset manually. Chilled water flow was measured with a portable ultrasonic flow meter installed in the chilled water supply loop. The data was analyzed, and an appropriate model of chiller performance was developed, as described below. 

The monitored data collected during the baseline period were used to develop the following model of the existing chiller performance. Because the performance depends on so many variables, the chiller models was based on ASHRAE energy efficiency Standard 90.1. The model is based on a set of bi-quadratic and quadratic equations, detailed in Equations 5-1, 5-2, and 5-3. 

The following notations are applicable to the equations used in this section:
CHWF
Chilled water flow in gallons per minute (GPM)

ECHWT
Entering chilled water temperature (return temperature, (F)

LCHWT
Leaving chilled water temperature (supply temperature, (F)

CWT
Condenser water temperature ((F) to chiller

PLR
Part Load Ratio

500
Conversion from GPM to pounds per hour Btu per pound-degree Fahrenheit 

12,000
Conversion from BTUH to tons 

CAPnom
Nominal full-load capacity of chiller (400 tons)

kWnom
Nominal full load chiller demand.  The nominal kW is the full-load rating multiplied by the nominal capacity (0.85 kW/ton ( 400 = 340 kW)

The maximum capacity (tons) of the chiller varies with operating parameters, and can be determined from Equation 5-1:

Equation 5-1: 


CAPt = CAPnom[a + b(CHWT) + c(CHWT)2 + d(CWT) + e(CWT)2 + f(CHWT)(CWT)]

In addition, the instantaneous chiller load and current part-load ratio are calculated by the following equations:

Equation 5-2:

TONSt = (CHWF)(500)(ECHWT – LCHWT)(1) / (12,000)

Equation 5-3:


PLRt = TONSt / CAPt
The baseline chiller electric demand is calculated with the following equations:

Equation 5-4:


EIRadj = g + h(CHWT) + i(CHWT)2 + j(CWT) + k(CWT)2 + l(CHWT)(CWT)

Equation 5-5:


PLRadj = m + n(PLRt) + o(PLRt)2
Equation 5-6:


kWt = (kWnom)(PLRadj)(EIRadj)

The ASHRAE model coefficients a through o for a water-cooled chiller
 are listed in the table below:
Table 5‑1: Chiller performance coefficients (water-cooled)
	
	a
	b
	c
	d
	e
	f

	CAPt
	-1.74204
	-0.029292
	-0.000067
	0.048054
	-0.000291
	-0.000106

	
	g
	h
	i
	j
	k
	l

	EIRadj
	3.1175
	-0.109236
	0.001389
	0.00375
	0.00015
	-0.000375

	
	m
	n
	o
	
	
	

	PLRadj
	0.222903
	0.313387
	0.46371
	
	
	


These calculations will be executed using a spreadsheet model. When estimating the baseline chiller performance, the actual chilled water temperature and tons will be used, along with a fixed condenser water temperature of 85°F. The baseline chiller currently operates at a fixed condenser water temperature and it is not appropriate to adjust the baseline to account for the new condenser water temperature strategy as the existing chiller could not take advantage of reduced condenser water temperatures because of physical operating limitations.
5.3 Proposed Energy & Water Savings Calculations and Methodology

The energy and demand savings will be calculated using Equations 5-7 and 5‑8, respectively.

Equation 5‑7

Energy Savings (kWh) = (t (kWht, baseline, est – kWht, measured, post )

= 0.25 ( (t (kWt, baseline –kWt,measured post)

Where:

kWt,baseline
=
demand that the baseline chiller would have used under the load conditions encountered for 15-minute interval t in the post-installation period

kWt, measured, post 
=
measured demand of the new chiller during 15-minute interval t.

Equation 5‑8

Monthly Demand Savings (kW) = MAX(kWt,baseline) – COINCIDENT(kWt,post)

Where:

MAX(kWt,baseline)
=
 maximum monthly demand of baseline chiller  predicted for each 15-minute interval in the peak period (between noon and 6 PM weekdays, May through October) during the current month using the model developed for the baseline chiller. 

COINCIDENT(kWt,post) 
=
measured demand of the new chiller during the period when the predicted baseline chiller demand was at its maximum value. 

Annual cost savings will be calculated using Equation 5-9.

Equation 5‑9:

Annual Cost Savings = Energy Savings (kWh) * RatekWh + 





(month(Monthly Demand Savings * RatekW)

where the rates are detailed in Table 2‑1 in Section 2.2. 
5.4 Operations and Maintenance and Other Cost Savings

O&M savings of $12,000 per year apply to this ECM. These cost savings are the result of ABC Engineering assuming the chiller maintenance contract for the new chiller. The cost of these annual services will be $14,000, compared to the existing contract for $26,000.

5.5 Proposed Annual Savings for ECM 
Proposed annual savings are summarized in the table below. Hourly bin calculations based on TMY weather data are included in the Appendix.
Table 5‑2: Proposed Annual Savings for ECM 3 – Chiller
	 
	Electric energy use (kWh/yr)
	Electric demand* (kW/yr)
	Total energy use (Mbtu/yr)
	Electric energy cost, Year 1 ($/yr)
	Electric demand cost, Year 1 ($/yr)
	Other energy-related O&M costs, Year 1 ($/yr)
	Total costs, Year 1 ($/yr)

	Baseline use
	500,004
	1,292
	1,707
	$26,250 
	$10,403 
	$26,000 
	$62,653 

	Post-installation use
	305,885
	790
	1,044
	$16,059 
	$6,364 
	$14,000 
	$36,423 

	Savings
	194,119
	502
	663
	$10,191
	$4,039
	$12,000
	$26,230


5.6 Post-Installation M&V Activities

After the new chiller has been installed and commissioned, ABC Engineering and Federal Center representatives will conduct a post-installation inspection to verify that the chiller installed is consistent with what was proposed and has the potential to generate the cost savings predicted. ABC Engineering will provide a Chiller Inspection Report detailing actual equipment installed, and include manufacturer’s specifications and operating procedures, chilled water and condenser water flows, and documentation of the chiller model number, and its rated and factory-tested efficiencies (in kW/ton). 

5.7 Performance Period Verification Activities

Post-installation monitoring of chiller demand and load variables (entering and leaving chilled water temperatures, chilled water flow rate, condenser water temperature) will be conducted for the entire contract period. This monitoring will be accomplished using the new building energy management and control system (EMCS). The EMCS will log and time-stamp the data at 15-minute intervals, saving the data weekly to disk. ABC Engineering will remotely download this data on a bi-monthly basis for back up and quality control. In the event that there is a significant gap in the data due to a sensor or other failure, the process to replace the missing data with interpolated or averaged data will be clearly documented.

Using the monitored post-installation data, the baseline energy use will be computed using the ASHRAE model and assuming standard (ARI) conditions as previously described.  
The new chiller’s performance will be compared to the manufacturers’ rated performance annually to ensure that the chiller is operating as expected. This will be accomplished by using the manufacturer’s performance curves, which are analogous to the ASHRAE performance curves used for the baseline chiller. The actual chilled and condenser water temperatures will be used with the manufacturer’s model. 
Some chiller performance degradation is expected over the course of the delivery order contract (5 years), which has been considered in determining the expected energy savings and the annual contract payments. If substantial equipment performance degradation occurs (>15% increase in annual energy use relative to the manufacturer’s model), the Agency will be responsible for taking the necessary maintenance actions to restore the chiller performance.

In the event of an unseasonably mild summer or change to the facility that decreases cooling load, the savings claimed will be based on a minimum cooling load of six hundred thousand ton-hours as defined by the typical monthly load curves included in the Appendix. 

Chiller demand: The chiller demand will be monitored using solid core current transducers and voltage leads connected to each leg of the chiller’s 3-phase circuit. All leads will be installed at the time of EMCS installation. These transducers will be installed on Breakers 1, 3 and 5 (the A, B and C phases) of Switch-Gear SW-1. Calibration of these sensors will be accomplished using an ACME True-RMS kW meter. Calibration of this parameter will be carried out once per year. 

Chilled water flow: Chilled water flow will also be monitored through the EMCS. At the time of chiller installation, an ACME inline flow meter will be installed in the chilled water loop. The flow meter is specified by the manufacturer to have an accuracy of (10%. The chilled water flow will be verified bi-monthly by downloading and checking data to identify sensors that have fallen out of calibration or to determine whether pump or chiller performance has degraded.

Condenser and chilled water temperatures: Water temperature sensors will be the insertion type, installed in new thermo-wells for both the condenser and chilled water temperatures. The sensors used will be ACME 2-wire, 1,000 OHM platinum RTDs paired with a 4-20 mA transmitter. The combined unit(s) will have an operating range of 20-120 (F with an accuracy of (0.50 (F. An annual field check of calibration will be conducted using the analog thermometers installed in the supply and condenser water lines. 

In addition to the calibration and testing procedures outlined above, all components will be tested and evaluated once each contract year. Also, the EMCS will continuously monitor the calculated kW/ton of the new chiller and issue an alarm when this value moves outside the expected range (0.40 - 1.10 kW/ton).

The data will be collected using quality control procedures for checking the measurements for reasonableness. Any and all missing intervals will be replaced either by interpolation or use of average values. Such data will be described in the Annual Report.

The Annual Report will summarize the calculated savings for the past year. Savings calculations will also be provided electronically, in MS Excel spreadsheets. All calculations will follow the procedure described in this M&V plan. In addition to the reports, all monitored data will be submitted in electronic format. 

The spreadsheet will show all intermediate steps in calculating baseline chiller kW, and show how energy savings will be determined. A sample spreadsheet format is provided in Figure 5.1, where variable names are described in the Chiller M&V Plan.

Table 5‑3: Sample Format of Baseline Calculations

	Measured Data
	Calculated Data



	Time
	ECHWT, (F
	LCHWT, (F
	CHW flow (GPM) 
	CWT, (F
	kWpost
	Tonst
	CAPt
	PLRt
	PLRadj
	EIRadj
	kWbase
	kWSaved

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	


Summary of Risk & Responsibility Matrix

	RESPONSIBILITY/DESCRIPTION
	PROPOSED APPROACH

	Financial:
	

	Interest rates: 
	ABC Engineering will work with the GSA to ensure that the best possible financial terms are secured for this project.

	Energy prices: 
	Energy prices for this DO have been set in the M&V plan. These rates are based on the current electric and natural gas costs for the Piscataway Federal Center, and are escalated at XX% based on NIST guidance.

	Construction costs:
	Construction costs are fixed and are the responsibility of ABC Engineering. If the DO is not awarded within 90 days of this proposal, these prices may be modified.

	M & V costs:  
	The M&V costs are fixed for the duration of the contract. ABC Engineering accepts all risks associated with performing the M&V activities as stated herein.

	Non-energy cost savings:
	Non-energy cost savings in this project are the result of the transfer of the chiller maintenance contract to ABC Engineering. Since the maintenance contract is the same length as the ESPC, no verification activities are scheduled.

	Delays:  
	ABC Engineering will work with the GSA to ensure delays are avoided and mitigated as much as possible. If delays are the result of GSA actions, ABC Engineering may submit a change order.

	Major changes in facility:
	No facility additions are planned for this time, however:

Lighting. Major renovations or additions to the facility could affect both the number of fixtures and their operating hours, with the possibility of causing the lighting energy costs to rise. The savings for this ECM are based on measured fixture powers and operating hours, values that will be held constant throughout th contract term. 

EMCS. In the event that changes are made to the building, the maximum operating hours for equipment has been defined in the M&V plan.

Chiller. In the event that the cooling load increases, the measured energy savings will also increase. If the annual cooling load decreases, , the minimum annual chiller use (in ton-hours) to calculate savings is specified in the M&V plan.


	RESPONSIBILITY/DESCRIPTION
	PROPOSED APPROACH

	Operational:
	

	Operating hours:  
	Lighting. Operating hours are based on monitored baseline data described in this plan. The post-retrofit period operating hours will be stipulated to be the same as the baseline period. Should the Agency change operating hours, the estimated savings will not change.

EMCS. ABC Engineering verified fan and pump motor operating hours for the baseline period, and will be responsible for monitoring operating hours in the performance period.  Maximum operating hours for equipment has been defined in the M&V plan in case of substantial change in schedule.

Heating setpoint will be set no higher than 68 ºF and cooling setpoint no lower than 72 ºF as agreed to by ABC and GSA. 

Chiller. ABC Engineering has estimated the load on the facility based on short-term monitoring and historical log data. The GSA is responsible for maintaining similar operating hours and load conditions in the post-installation period, and agrees that the chiller will be used annually for the minimum number of ton-hours defined in the M&V plan. If operating ton-hours increase, measured savings will also increase.

	Load:  
	EMCS. Increase in loads may result in use of maximum operating hours specified in the M&V plan. Savings from reduced chiller operation between 9:00 PM and startup will accrue to the EMCS measure. Savings are based on measured chiller operation. 
Chiller. In the event that the cooling load increases, the measured energy savings will also increase. If the annual ton-hours of the new chiller falls below the amount specified in the baseline, the chiller savings will be calculated using the minimum defined in the M&V plan.

	Weather:  
	Chiller. Although the operation of the new chiller may be affected by weather conditions, no weather corrections are to be performed. If mild conditions result in reduced chiller loads, the loads may be adjusted upwards. 

	User participation:
	Lighting & Chiller: The savings for the lighting and chiller ECMs are based on the continuation of the current operating strategies. This responsibility is accepted by the Agency.

EMCS: The savings from the operation of the EMCS is based on the control sequences outlined herein. Since these control sequences could be overridden by the facility operating staff, the Agency accepts responsibility that the EMCS will continue to operate as specified.


	RESPONSIBILITY/DESCRIPTION
	PROPOSED APPROACH

	Performance:
	

	Equipment performance:
	Lighting. ABC Engineering is responsible for ensuring that the new lamps and ballasts are as specified for the first performance year and meet the Energy Policy Act of 2005 requirement in terms of minimum performance specifications. After this point, the Agency assumes this responsibility.

EMCS. The Agency is responsible for maintaining the fan and pump motors so that the power draws remain at the baseline level.

Chiller. The chiller is expected to perform as rated by the manufacturer for the term of the contract and meets the Energy Policy Act of 2005 requirement in terms of minimum performance specifications. The GSA is responsible for maintaining all central plant equipment, with the exception of the new chiller, for the duration of the contract. Chiller performance will be verified by ABC Engineering during commissioning and checked annually for the duration of the contract.

	Operations:  
	The Agency accepts responsibility for the ongoing operation of the equipment and systems affected by this DO, as described herein.

	Preventive maintenance: 
	The Agency accepts responsibility for the ongoing maintenance of all equipment affected by this DO, with the exception of the new chiller. ABC Engineering will conduct annual inspections of the affected equipment, and will report any discrepancies and suggested remedies to the Agency immediately. ABC Engineering will perform preventive chiller maintenance under a separate contract with GSA. Annual calibration of chilled-related sensors will be performed as part of this maintenance contract. 

	Equipment repair and replacement: 
	Lighting. ABC Engineering is responsible for replacement of failed, defective, or burned-out lamps and ballasts for the first contract year. The Agency is responsible for replacement of failed or burned-out lamps and ballasts after the first year. Normal lifetimes of lamps are 15,000 to 20,000 hours when connected to electronic ballasts. Electronic ballast lifetimes are expected to be from 5 to 8 years.

EMCS. The fan and pump motors will not be changed as part of this project, only control of the motors will be added. The motors are expected to last throughout the term of this contract, but if they should fail, the Agency is responsible for their replacement and commissioning. Savings will be calculated based on the baseline power measurements.

Chiller. Expected life of the chiller substantially exceeds the contract length. The manufacturer’s warranty will determine what coverage will apply in the event of premature failure. 


� FEMP M&V Guideline V 2.2 available at �HYPERLINK "http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html"��http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html�


� M&V Plan Outline for FEMP Super ESPC projects is available at �HYPERLINK "http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html"��http://www1.eere.energy.gov/femp/financing/superespcs_mvresources.html�





� NISTIR 85-3273-17 (Rev. 4/01) Energy Price Indices and Discount Factors for Life-Cycle Cost Analysis – April 2002, Annual Supplement to NIST Handbook 135 and NBS Publication 709


� http://www.njsmartstartbuildings.com/main/equip_inc.html


� See Appendix D – Sampling Guidelines, pages 321 & 322 of M&V Guidelines: Measurement and Verification for federal Energy Projects, Version 2.2.


� This is not an arbitrary rule, but an observation that a population with a Cv of 0.2 has a range if about 2:1 between the highest and lowest values. If the ratio is greater than 2:1, it is very probable that the Cv is greater than 0.2. 


� See Attachment 4.


� ASHRAE / IES Standard 90.1-1989 User's Manual American Society of Heating, Refrigeration, and Air Conditioning Engineers. Atlanta, GA. 1992





8

M&V Plan and Savings Calculations Methods


Page 38
 


_1222695986.unknown

_1225027216.unknown

_1225027759.unknown

_1225026523.unknown

_1216449514.unknown

_1218960518.unknown

