## Slide 1
BPSA Wastewater Flow Projections
Review of COG’s Round 9.0 Flow Projections, Estimated Projections for Round 9.1, & RWFFM Methodology Update
Nasser Ameen WRTC March 8, 2018
Blue Plains 2012 IMA
District of Columbia
District of Columbia – Water and Sewer Authority
Fairfax County
Montgomery County
Prince George's County
Washington Suburban Sanitary Commission

## Slide 2
Overview & Schedule
Round 9.0 & Round 8.4 – Comparison of Previously Approved data
Schedule for Round 9.1 Approval
Round 9.0 vs 9.1 – Changes in Demographics
ChesBay Program’s 2025 Flow Projections vs. Round 9.0/2025
Planned Updates of RWFFM/BPSA Methodology
Round 9.0
  Formally approved by the COG Board on Nov. 6th 2016
  Formally approved by TPB on Nov. 15th 2016
  Round 8.4 stops at 2040, where as Round 9.0 expands planning horizon another 5 years, to 2045
  Reflects demographic updates from all COG members
Round 9.1
  Will be officially approved in the Fall of 2018
  Only a few COG member have submitted updated data

## Slide 3
Round 8.4/Round 9.0 Comparison
 | 2009 | 2010 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045
Round 9.0 BP Adjusted Total Flow | 296.55 | 293.62 | 304.11 | 313.39 | 321.78 | 335.09 | 345.98 | 355.35 | 364.49
Round 8.4 BP Adjusted Total Flow | 296.55 | 294.92 | 305.86 | 314.66 | 323.47 | 334.92 | 345.93 | 356.01 | 
Round 9.0 Major WWTP COG Region | 549 | 553.53 | 586.57 | 622.22 | 659.01 | 692.87 | 721.66 | 748.1 | 774.5
Round 8.4 Major WWTP COG Region | 553.25 | 559.55 | 592.06 | 630.85 | 668.46 | 703.78 | 733.97 | 760.93 | 
370 MGD does not include CSFs
Chart: Round 8.4 vs Round 9.0
| 2009 | 2010 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045
Round 9.0 BP Total Flow | 296.55 | 293.62 | 304.11 | 313.39 | 321.78 | 335.09 | 345.98 | 355.35 | 364.49
Round 8.4 BP Total Flow | 296.55 | 294.92 | 305.86 | 314.66 | 323.47 | 334.92 | 345.93 | 356.01
Round 9.0 Major WWTP COG Region | 549 | 553.53 | 586.57 | 622.22 | 659.01 | 692.87 | 721.66 | 748.1 | 774.5
Round 8.4 Major WWTP COG Region | 553.25 | 559.55 | 592.06 | 630.85 | 668.46 | 703.78 | 733.97 | 760.93

## Slide 4
Round 9.1 – Updated Schedule
COG Board is planning to officially approve the Round 9.1 data this coming fall of 2018
COG staff will begin generating our flow projections using our Regional Wastewater Flow Forecast Model
  Once we generate our flow projections, it will be treated as “unofficial” data projections that can be shared only as an “internal” document
The Transportation Planning Board (TPB) have used their model to run Round 9.1 and generate demographic projections
  These demographic projections, which include other counties outside of COG Jurisdiction, show only a slight change when compared to Round 9.0
  It is important to note that the changes only provide an estimated glimpse of the Round 9.1 demographic projections, as we have yet to use our model to run the numbers

## Slide 5
Change in 2045 Between Round 9.0 and Round 9.1
TPB Model Region
(Thousands)
Round 9.0 Round 9.1 Number Percent
Employment 5,515.9 5,507.3 -8.6 -1.6%
Population 9,083.9 9,120.9 37.0 0.4%
Households 3,475.6 3,487.7 12.1 0.4%

## Slide 6
Chesapeake Bay Program vs. COG - 2025 Flow Projections
ChesBay Program generated draft flow values for 2025 using their current draft methodology
  It was developed as a supplemental aid to states in planning their Phase 3 WIPs (some question if really needed)
  It responds to the question “Where will the actual flows and loads from the WWTPs will be in 2025?”
  https://www.chesapeakebay.net/channel_files/25900/projection2025_growth_w_wip_caps_draft.xlsx
COG-wide RWFFM projected flow values for 2025
  640.63 MGD (83% of Design Capacity)
CBP projected flow values for 2025
  556.6 MGD (72% of Design Capacity)
Question – What is intent/appropriate use of either of these methods?

## Slide 7
COG Region Major (=/>2 mgd) WWTPs Summary |  |  |  |  | (as of 3/9/18) |  | 
Major WWTPs (alpha. order by state) | STATE | Design Capacity (MGD) | ENR/SOA Implementation Schedule (as of 12/6/2016) | Annual Average Flows (MGD) |  |  | 
 |  |  |  | 2016 DMR Flow1 | Projected Flows |  | 
 |  |  |  |  | 2025 COG RWFFM Method (Rd 9.0)2 | 2025 CBP Draft Method3 | 2045 COG RWFFM Method (Rd 9.0)2
Blue Plains4 | DC | 370 | 2018 | 275.3 | 321.79 | 298.74 | 364.49
Ballenger Creek | MD | 6 | 2014 | 6.84 | 5.84 | 6.32 | 6.8
Bowie | MD | 3.3 | 2011 | 1.54 | 2.26 | 1.9 | 2..63
Fort Detrick | MD | 2 | 2011 | 0.85 | 0.73 | 0.91 | 0.81
Frederick | MD | 8 | 2017 | 6.42 | 8.18 | 6.38 | 8.89
Mattawoman | MD | 20 | 2007 | 9.88 | 13.18 | 11.09 | 13.33
Parkway | MD | 7.5 | 2013 | 6.4 | 6.75 | 6.86 | 6.86
Piscataway | MD | 30 | 2012 | 24.86 | 23.3 | 24.77 | 24.96
Seneca Creek | MD | 26 | 2017 | 14.42 | 19.4 | 15.85 | 21.94
Western Branch | MD | 30 | 2017 | 19.14 | 23.3 | 20.88 | 26.11
Alexandria | VA | 54 | 2015 | 32.72 | 42.12 | 35.95 | 52.33
Arlington | VA | 40 | 2011 | 22.93 | 31.76 | 23.59 | 40.64
Broad Run5 | VA | 11 | 2021 | 4.05 | 9.94 | 4.3 | 14.6
Dale City | VA | 9.2 | 2013 | 5.63 | 7.83 | 6.02 | 9.05
H.L. Mooney | VA | 24 | 2013 | 13.84 | 23.26 | 14.34 | 29.68
Leesburg | VA | 7.5 | BNR only - No ENR | 4.09 | 6.51 | 4.5 | 7.4
Noman Cole6 | VA | 67 | 2013 | 36.92 | 55.76 | 40.06 | 77.21
UOSA | VA | 54 | 2014 | 32.1 | 38.72 | 34.14 | 48.28
TOTAL |  | 769.5 |  | 517.93 | 640.63 | 556.6 | 753.38
% of Design Capacity |  |  |  | 67% | 83% | 72% | 98%
Blue Plains Projected Flows reflect 'Demographically Driven & Flow Management Adjusted' figures for BPSA, w/out Captured Stormwater Flows

## Slide 8
Planned Updates of RWFFM/BPSA Assumptions & Methodology
RWFFM is used for long-term planning purposes for the BPSA, & for confirming/portraying future flows for the overall COG region
    Being evaluated in 2018 for potential modifications
COG staff is gathering wastewater flow methodology information and related from the Blue Plains Users and others across the region
COG staff will use that to draft a scope of work for consultant support to assess all aspect so forecasting wastewater flows
  Plan is to initiate contract in next few months

## Slide 9
Planned Updates of RWFFM/BPSA Assumptions & Methodology
Current BPSA Flow Factors |  |  |  |  |  | 
Category / Jurisdiction | Revised Fairfax | WSSC | Loudoun Water | District | Dulles | Vienna
Household (gpd/unit) | 151 | 180 | 185 | 170 | N/A | 170
Employment (gpd/employee) | 21 | 28 | 25 | 25 | 48 | 21-50
*the incremental I/I rate of 44% would remain the same from 2001 study |  |  |  |  |  | 
Intention is to evaluate all aspects of current RWFFM (updated in 2001)
  Base Year – Use actual 2009 flows
  Inflow/Infiltration – Continue to use 44%
  Flow Factors (below)

## Slide 10
Recap & Future Dates
As mentioned earlier, COG will officially approve of the Round 9.1 data in October 2018
We are still working with Jurisdictions/agencies to:
  Provide us with their flow methodology, and
  Confirm their flow and ENR/SOA information
We anticipate issuing a contract for consultant services in the next few months

## Slide 11
Nasser Ameen (202) 962-3394 ameen@mwcog.org | mwcog.org
777 North Capitol Street NE, Suite 300 Washington, DC 20002 |