## Slide 1
WASHINGTON D.C. METROPOLITAN AREA BACKUP WATER SUPPLY Feasibility Study
Briefing for the Water Resources Technical Committee (WRTC) January 9, 2026
COG

## Slide 2
Regional Water Supply Study Partners
Metropolitan Washington Council of Government​
USACE Baltimore District
Washington Aqueduct
DC Water​
Arlington County
Fairfax Water​
WSSC Water
Interstate Commission on the Potomac River Basin
WRTC Briefing:
January 9, 2026

## Slide 3
Regional Cooperative Water Supply System
*A Division of the US Army Corps of Engineers
Suppliers
Fairfax Water
WSSC Water
Washington Aqueduct*
Off-Potomac Sources
Fairfax Water: Occoquan
WSSC Water: Patuxent
Shared Reservoirs
Jennings Randolph
Little Seneca
Savage
WRTC Briefing:
January 9, 2026

## Slide 4
Regional Water Supply System
Potomac River Supplies 78% of the Region’s Water Supply
Goose Creek
Quarry A (Milestone Reservoir)
Potomac River
Patuxent Reservoirs
Occoquan & Vulcan Reservoirs
Rockville
Leesburg
Fairfax Water
Loudoun Water
Frederick County
WSSC Water
Virginia American
Alexandria and Dale City
Arlington Co.
DC Water
Vienna
Prince William Co. Service Authority
Howard Co.
Charles Co.
Creeks & Wells
Washington Aqueduct
Ft. Belvoir
Dulles Airport
Herndon
Emergency
City of Bowie
DC Water
WRTC Briefing:
January 9, 2026

## Slide 5
21st Century Resiliency Planning
Two primary considerations
Spill releases into river
Unprecedented drought due to climate change.
Total loss of Potomac Water supply would cripple region and federal government
All of DC and Arlington would lose water after one day
Many Fairfax Water and WSSC Water customers would lose service within days
WRTC Briefing:
January 9, 2026

## Slide 6: Contamination Risk
CONTAMINANT SOURCES
Colonial Pipeline leak into the Potomac River
Colonial Pipeline or other leak into a Potomac Tributary
Upstream industrial sources (Paper Mill, Power Plant closed 2020)
Railroad crossing at Harpers Ferry
Bridge crossings
Deliberate contamination
There have been seven contamination events since 1980 that have posed a risk to WMA supply.
Recent Events:
2024, July – Algae Causes Turbidity Spike and Precautionary Boil Water Advisory
  2025, April – Tanker Truck Spill into Difficult Run, a Potomac River Tributary
WRTC Briefing:
January 9, 2026

## Slide 7
Harper’s Ferry 2019
CSX Train Derailment
WRTC Briefing:
January 9, 2026

## Slide 8: Drought
Potomac River intakes
Little Seneca Reservoir
Jennings Randolph Reservoir
Savage Reservoir
West
Virginia
Pennsylvania
Maryland
Virginia
District
of
Columbia
2024-2025 Drought Watch
  Moderate to Severe Drought
  38-day period with no precipitation in 2024 (longest on record)
  Lasted nearly one year
CO-OP Reservoirs:
Jennings Randolph Reservoir (USACE)
Savage Reservoir (releases by USACE)
Little Seneca Reservoir (WSSC)
Travel-time from Jennings Randolph
Reservoir to the DC area is 7-9 days
WRTC Briefing:
January 9, 2026

## Slide 9: Opportunities
Within this study, there are opportunities to:
Decrease water supply dependance on the Potomac River during contamination and drought events
Improve the ability of water suppliers to respond to spills and drought
Incorporate infrastructure improvements (modernize, interconnect, create redundancy, increase system flexibility for future expansion) into water supply systems
Increase water supply system resilience to multiple types of disruption
Improve public understanding of water supply disruption and responses (e.g., demand reduction, prioritization of water uses)
Increase the resilience of water supply dependent national security and critical infrastructure
WRTC Briefing:
January 9, 2026

## Slide 10: Existing & Future without project
WATER DEMAND & AVAILABILITY
Water demand averaged 463 million gallons per day (MGD) for the WMA and 431 MGD for the CO-OP suppliers during the most recent period of data availability (2018-2023).
There is a lot of uncertainty regarding water demand forecasting.
Forecasts indicate water demand will increase with increased population growth. Population for the WMA is forecast to increase by 20% by 2050, with water demand to increase similarly (17%).
Mean precipitation for 2040-2050 is projected to increase by about 10%.
Mean temperature expected to increase by 5.2°F.
There is large uncertainty about how hydrometeorological changes will affect stream flow and water availability.
(ICPRB 2025)
Water Supply System Reliability under Flow Scenarios (ICPRB, 2020)
2040
2050
Under all Low Flow Scenarios, system is in failure without additional raw water source.
Medium Flow Scenario:
  System reliability is marginal in 2040 but could be reliable with operational changes.
  System is unreliable in 2050.
System Reliability (demand & river flow)
WRTC Briefing:
January 9, 2026
Notes: -ICPPRB is the regional authority on water demand and forecasting. They conduct a Water Demand Forecast every 5 years and they are updating it this year. Average water demand for WMA is about 464 MGD, with the bulk of that coming from the COOP suppliers. The population for the WMA is projected to increase 14% by 2040, and water demand is expected to increase similarly.
-Precipitation for 2040-2050 is projected to increase by 8-10%, and temperatures are expected to increase by 4-5 degrees.
-There is large uncertainty as to how this will affect stream flows. It will depend on whether it is precipitation or temperature that dominates the system.
-As this relates to water supply system reliability, ICPRB projects that at low river flow, the water supply system is unreliable for all demand scenarios. For medium river flow with medium demand, the system is marginal, but would be unreliable during high demand.

## Slide 11: Alternatives formulation
13-17 January 2020: USACE Value Planning Study
21 August 2024: Charrette - Problems, Objectives, Constraints, Considerations, etc.
December - January 2025 – Measures refinement and additions, soliciting comments from water utilities
24 January 2025: Charrette – Measures Screening
24 February 2025: Charrette – FWOP conditions, functional requirements for backup supply
March - April 2025: Team formulation and screening of alternatives with feedback from water utilities
06 June 2025: Study update and screening discussion
WRTC Briefing:
January 9, 2026

## Slide 12: Measures/strategy screening
Alternative Strategies | Description | 
New Reservoir Storage | Acquire and develop new reservoir | Retain
Existing Reservoir Modification | Deepen, widen, raise pool elevation in existing reservoirs | Screen
Direct or indirect wastewater reuse | Use treated water from Blue Plains Advanced Wastewater Treatment Plant (AWWTP) and pipe to reservoirs or use directly | Retain
Desalination | Withdraw water from the estuary for desalination | Screen
Groundwater use | Withdraw groundwater, with or without augmentation/injection of treated water from Blue Plains AWWTP | Screen
Stormwater use | Connect to stormwater system and convey water to treatment plant | Screen
Diversion from another source | Divert water from another basin, reservoir, or river (e.g., Liberty Reservoir, Susquehanna River Basin, Little Seneca) | Screen
New or enhanced water treatment | Enhanced water treatment to address most probable contaminants | Screen
Enhanced interconnections, tunnels, or intakes | Connect existing infrastructure to create flexibility in transferring water throughout the system; modify/add intakes; connect to existing reservoirs | Retain
Increased finished water storage | Add finished water storage at water treatment plants or critical locations | Screen
Non-Structural Measures | Planning or operational measures that reduce risk and vulnerability | Use for recommendations
WRTC Briefing:
January 9, 2026
Notes: In coordination with the stakeholders at a workshop, we discussed the measures and strategies and screened them based on best professional judgment in terms of feasibility, acceptability, or impacts. The numbers in parentheses show the numbers of measures we started with and then number that we were reduced to after screening. A few of the strategies fell out once all the measures in that strategy were screened.
The strategies that fell out were:
-Groundwater use: This was removed because the extended team felt that this was infeasible and likely unacceptable. A well field required to install the number of wells needed to meet even a small part of the water demand would be excessive. It would be expensive, require a great deal of land, and result in unacceptable impacts to resource agencies.
-Stormwater use: The measures here included connecting to the stormwater system to capture and use stormwater. The team felt this would in impractical and infeasible given the massive collection, pumping, storage, and transmission systems needed to convey this water. It could introduce contaminants that may not be easy to treat and would not be reliable under drought conditions.
-New or Enhanced Water Treatment – these measures involved modifying treatment plants or installing new treatment systems to mitigate for the most probably contaminants. This seemed an expensive option for a guess at what the contaminant could be and also does not mitigate for drought conditions.
-Increased finished water storage – there were two measures to increase finished water storage capacity at treatment plants or at critical facilities, but both of those are problematic due to regulatory constraints regarding finished water and the amount of time you are allowed to store water to maintain water quality to prevent the formation of disinfection byproducts.
-Finally non-structural measures will be retained for recommendations to supplement any structural alternatives.

## Slide 13: Focused Array of Alternatives
Alternative Components
No Action
Travilah Quarry - Acquire and develop into a raw water reservoir.
Blue Plains AWWTP - Indirect or direct wastewater reuse for secondary water source
Luck Stone Quarry B - Build and acquire for additional storage.
Luck Stone Quarry C - Build and acquire for additional storage.
Dalecarlia WTP Reservoir – expansion for additional storage (would only benefit DC Water)
Luck Stone Quarry: Leesburg Plant (photo credit: Luck Stone)
Luck Stone Quarry: Goose Creek Plant (photo credit: Luck Stone)
Travilah Quarry (photo credit: Aggregate Industries)
Blue Plains AWWTP (photo credit: DC Water)
WRTC Briefing:
January 9, 2026

## Slide 14: Phase of study
AMM = Alternatives Milestone Meeting
TSP = Tentatively Selected Plan Milestone
CVM = Command Validation Milestone
Alternatives Milestone
Project Management Plan
Cost-sharing Coordination
Stakeholder Coordination
Existing Conditions
Initial Project Alternatives & Screening
Tentatively Selected Plan
Final Alternatives Development
Conceptual Costs
& Design
Agency Decision
Draft Report Finalization
Detailed Design and Final Report
Alternatives Milestone
Economic Analysis
Plan Recommendation
Draft Report Preparation
Tentatively Selected Plan Milestone
Model Analysis
Internal Report Review
Public Report Review
Command
Validation Milestone
Feasibility-Level Design
Report Updates
Report Finalization & Reviews
Senior Leaders Panel
State and Agency Review
Report of the Chief of Engineers
Scoping and Problem ID
Alternatives Analyses
Draft Report Review
Detailed Designs and Final Report
TSP
28 March 2024
Scoping
Alternatives
Formulation
& Analysis
Feasibility
Level Analysis
Washington
Level Review
AMM
CVM
Chief's Report
12 June 2025
WRTC Briefing:
January 9, 2026

## Slide 15: Study Schedule
Milestone | Current P2 Schedule*
Feasibility Cost Share Agreement (FCSA) Execution | 30 September 2024 (A)
Interagency Meeting | 10 February 2025 (A)
Alternatives Milestone (CW261) | 12 June 2025 (A)
Vertical Team Alignment Memorandum (VTAM) | 12 August 2025
Tentatively Selected Plan (TSP) (CW262) | TBD (contingent on receipt of Fed Funds)
Release Draft Report for Public Review | TBD
Command Validation Milestone (CVM) (CW263) | TBD
Final Report Transmittal from MSC to HQ (CW260) | TBD
Chief’s Report (CW270) | TBD
WRTC Briefing:
January 9, 2026

## Slide 16
Any Questions?
WRTC Briefing:
January 9, 2026

## Slide 17
Steve Bieber Water Resources Program Director (202) 962-3219 / sbieber@mwcog.org | mwcog.org
777 North Capitol Street NE, Suite 300 Washington, DC 20002 | 
WRTC Briefing:
January 9, 2026